## Slide 1
Technical Methodology
Demand Estimation & Least-Cost Electrification Model for Benin

## Slide 2
Demand Model — Assumptions & Formulas
Framework: World Bank Multi-Tier Framework (MTF)
Tier 1: 22 kWh/hh/yr Tier 2: 73 Tier 3: 365 Tier 4: 730 Tier 5: 2190
Tier assignment per settlement (heuristic):
pop >= 10 000 or nightlight --> Tier 5
pop >= 3 000 or (1 000 + nightlight + services) --> Tier 4
pop >= 500 or (200 + services) or dist < 5 km --> Tier 3
pop >= 100 or services or dist < 15 km --> Tier 2
else --> Tier 1
Residential demand (year t):
D_res(t) = connections(t) * tier_kWh * (1.05)^t / 1000 [MWh]
Productive: D_prod = D_res * 0.20 (shops, mills, irrigation)
Institutional: D_inst = D_res * 0.10 (schools, health centres)

## Slide 3
Demand Model — Growth & Electrification
Planning horizon: 10 years (2024-2034)
Population growth: 2.7 %/yr (World Bank WDI, Benin)
Per-connection demand growth: 5 %/yr (IEA Africa Energy Outlook)
Household size: 4.5 people (DHS West Africa surveys)
Electrification rate growth:
Linear ramp from initial rate to 100 % by 2034 (SDG7 target)
Initial rate varies by proximity to grid:
dist < 2 km: 60 % dist < 10 km: 35 %
dist < 30 km: 15 % dist > 30 km: 5 %
Total demand = Residential + Productive (20%) + Institutional (10%)
Key difference from OnSSET: we add productive & institutional demand
(OnSSET models residential only; this is our modification)

## Slide 4
Technology Cost Assumptions
Parameter | Grid | Mini-grid | SHS
CAPEX | $7,000/km line | $3,500/kW | $150–1,500/sys
Connection cost | $200/hh | $400/hh | Included
OPEX (% CAPEX/yr) | 3% | 5% | 2%
Discount rate | 10% | 10% | 10%
Lifetime | 30 yr | 20 yr | 10 yr
Max distance | 50 km | — | —
Pop. range | Any | 50–10,000 | Any (Tier 1–3)
T&D losses | 15% | — | —
Gen. cost | $80/MWh | — | —
Sources: OnSSET defaults [Mentis 2017], IRENA 2023, SEforALL mini-grid benchmark 2024 |  |  | 

## Slide 5
LCOE Formulation
LCOE = NPV(Total Costs) / NPV(Energy Delivered) [USD/MWh]
NPV = SUM( value_t / (1 + r)^t ) for t = 0 .. T
r = 10 % (OnSSET standard for SSA)
Cost stream for each technology:
Year 0: CAPEX + OPEX_0
Year t>0: OPEX_t * (1.02)^t + replacements (if scheduled)
Grid: OPEX includes energy purchase at $80/MWh (grid tariff)
Energy delivered adjusted for 15 % T&D losses
Mini-grid: Battery replacement at year 7 (40 % of gen CAPEX * 0.7)
SHS: Battery replacement at year 5 (35 % of system * 0.8)
Least-cost selection: technology with minimum LCOE wins

## Slide 6
Results Summary
17197
Settlements
13,968,034
Population
13,530,363
MWh demand (2034)
Grid: 5275 settlements (31 %) median LCOE $5,350/MWh median CPC $2,145
Mini-grid: 300 settlements (2 %) median LCOE $1,882/MWh median CPC $628
SHS: 11622 settlements (68 %) median LCOE $1,162/MWh median CPC $400
Tier distribution: Tier1: 3928 | Tier2: 6940 | Tier3: 5837 | Tier4: 255 | Tier5: 237

## Slide 7
OnSSET Modification: Productive & Institutional Demand
Standard OnSSET approach:
Models residential demand only
Single MTF tier per country
No settlement differentiation
Our modification:
Added productive demand (+20 %)
Shops, grain mills, irrigation
Added institutional demand (+10 %)
Schools, health centres
Settlement-differentiated tiers
Based on pop, distance, services
Impact of modification:
Total demand increases by 30 %
Shifts some settlements from SHS
to mini-grid (higher peak load)
More realistic representation of
actual rural energy needs
Implementation:
D_total = D_res * (1 + 0.20 + 0.10)
Applied uniformly to all settlements
Could be refined with local surveys

## Slide 8
Least-Cost Decision Logic & Prioritisation
For each settlement:
1. Estimate demand (tier + growth + productive + institutional)
2. Check viability constraints:
Grid: distance <= 50 km
Mini-grid: 50 <= population <= 10,000
SHS: demand tier <= 3 (SHS cannot serve Tier 4-5)
3. Compute LCOE for each viable technology
4. Select technology with lowest LCOE
Priority scoring (for settlement ranking):
Priority = 0.40 * pop_norm + 0.25 * infra_score
+ 0.20 * cost_effectiveness + 0.15 * grid_proximity
Where infra_score = 0.6 * has_health + 0.4 * has_education

## Slide 9
Sensitivity Analysis — Actual Results
Method: One-at-a-time (OAT). Base case: Grid 23% / Mini-grid 0.9% / SHS 76% / Mean LCOE $1,434/MWh
Discount Rate Grid: 23–23% (±0.0pp) SHS: 76–76% LCOE: $1,129–$1,795
Grid Line Cost Grid: 20–28% (±4.1pp) SHS: 71–79% LCOE: $1,406–$1,455
SHS System Cost Grid: 19–26% (±3.2pp) SHS: 70–81% LCOE: $1,110–$1,743
Demand Growth Rate Grid: 23–23% (±0.1pp) SHS: 72–77% LCOE: $1,131–$1,711
Mini-grid PV+Battery Cost Grid: 22–23% (±0.8pp) SHS: 72–77% LCOE: $1,428–$1,435
Key findings:
Grid line cost has the largest impact on technology mix (±4 pp)
SHS cost shifts Mini-grid share most (0–5% range)
Demand growth mainly affects LCOE, not technology choice
Discount rate affects LCOE strongly but not which tech wins
Mini-grid cost drives its own viability (disappears above $4,000/kW)

## Slide 10
Sensitivity Analysis — Technology Mix by Parameter
Summary of most sensitive parameters (impact on % settlements per tech):
Parameter | Grid swing (pp) | SHS swing (pp) | MG swing (pp) | LCOE range
Grid Line Cost | ±4.1 | ±4.0 | ±0.2 | $1,406–$1,455
SHS System Cost | ±3.2 | ±5.6 | ±2.4 | $1,110–$1,743
Mini-grid PV+Battery Cost | ±0.8 | ±2.2 | ±3.0 | $1,428–$1,435
Demand Growth Rate | ±0.1 | ±2.2 | ±2.2 | $1,131–$1,711
Discount Rate | ±0.0 | ±0.0 | ±0.0 | $1,129–$1,795

## Slide 11
Code Architecture
Python implementation (benin_electrification.py, ~600 lines):
Functions (not classes — kept simple per assignment guidance):
assign_demand_tier() Heuristic tier assignment per settlement
estimate_demand() 10-year demand projection (DataFrame)
cost_grid() Grid extension LCOE + cost/connection
cost_minigrid() Mini-grid (solar PV) LCOE + cost/connection
cost_shs() Solar Home System LCOE + cost/connection
analyze_settlement() Orchestrates demand + costs + selection
run() Main entry point; loops all settlements
Supporting script:
run_analysis.py Pipeline: runs analysis + generates 6 charts
create_presentations.py This script; generates PPTX decks
Dependencies: numpy, pandas, matplotlib, python-pptx

## Slide 12
Limitations & Future Enhancements
Model limitations:
Tier assignment is heuristic
No hourly load profiles
Fixed cost assumptions
No grid capacity constraints
No technology switching over time
Diesel backup not modelled
Single household size (4.5)
With more time / data:
Calibrate tiers with survey data
Add solar irradiance (GHI) maps
Model grid congestion / feeders
Include affordability analysis
Run full OnSSET with GEP data
Add diesel hybrid mini-grids
Implement Monte Carlo sensitivity
GIS visualisation of results

## Slide 13
References
[1] Mentis et al. (2017) 'Lighting the World: OnSSET on SSA'
Environmental Research Letters, 12:085003
[2] Korkovelos et al. (2023) 'Cost of electrifying 40 SSA countries'
Nature Communications, 14:4769
[3] IRENA (2023) Renewable Power Generation Costs
irena.org/publications
[4] World Bank Multi-Tier Framework for Energy Access
seforall.org/publications
[5] OnSSET documentation: onsset.readthedocs.io
[6] SEforALL (2024) Mini-grid CAPEX/OPEX Benchmark Study